## MDH
Electrical wiring 0f Repair & renovation of electrical Wiring/ replacement of damaged Accessories in "MDH" quarters residential complex of IGIMS, Patna
Sl.No. | DSR-14 | Items | Qty. |  | Rate | Total
1 | 1.8 | Wiring for light point/fan point /exhaust fan point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/recess P.V.C. conduit with piano type switch, phenolic laminated sheet, suitable size pvc / gi box etc. as required.
a) | 1.8.1 | Group-B | 102 | Nos. | 543 | 55386
2 | 1.12 | Wiring for light/power plug with 2 x 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/ recessed P.V.C. conduit along with 1-No. 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable for loop earthing as required. | 280 | MT | 162 | 45360
3 | 1.14 | Wiring for cirucit/sub-main wiring alongwith earth wire with the following sizes of P.V.C. insulated copper conductor, single core cable in surface/recessed pvc conduit, as required.
a) | 1.14.1 | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | 930 | MT | 106 | 98580
b) | 1.14.3 | 2 x 4 sq.mm + 1 x 4 sq.mm. earth wire | 350 | MT | 162 | 56700
c) | 1.14.5 | 2 x 10 sq.mm + 1 x 10 sq.mm. earth wire | 95 | MT | 327 | 31065
4 | 1.15 | Rewiring for light point /fan point /exhaust point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conducotr single core cable in existing surface/recessed P.V.C. conduit including dismantling as required.
a) | 1.15.2 | Group-B | 168 | Nos. | 303 | 50904
5 | 1.17 | Supplying and drawing following of F.R. P.V.C. inulated copper conductor single core cable in existing surface/recessed P.V.C. conduit, as required.
a) | 1.17.1 | 1 x 1.5 sq.mm | 450 | MT | 22 | 9900
b) | 1.17.2 | 2 x 1.5 sq.mm | 400 | MT | 36 | 14400
c) | 1.17.3 | 3 x 1.5 sq. mm | 1690 | MT | 50 | 84500
d) | 1.17.21 | 3 x 4 sq.mm | 390 | MT | 109 | 42510
6 | 1.23 | Supplying and fixing following piano type switch/socket on the existing switch box/cover including connection etc. as required
a) | 1.13.1 | 5/6 amps.one way Switch | 270 | Nos | 33 | 8910
b) | 1.13.3 | 15/16 amps.one way Switch | 40 | Nos | 72 | 2880
c) | 1.13.4 | 5/6 amps.5 pin Socket out let | 90 | Nos | 41 | 3690
d) | 1.13.5 | 15/16 amps.6 pin Socket out let | 40 | Nos | 83 | 3320
7 | 1.29 | Supplying and fixing suitable sizes GI / PVC box on surface or in recess with phenolic laminated sheet cover in-front incluidng providing and fixing 5 pin 05/06 amps. Socket outlet and 05/06 amps. Piano type switch connection painting etc. as required. | 55 | Nos | 194 | 10670
8 | 1.3 | Supplying and fixing suitable size of GI / PVC box on surface or in recess with phenolic laminated sheet cover infront including providing and fixing 6 pin 5/6 amps. & 15/16 amps. Socket outlet and 15/16 amps piano type switch connection, painting etc. as required. | 58 | Nos | 276 | 16008
9 | 2.1 | Supplying and fixing following rating 240 volts 'C' series M.C.B. 5 Amps to 32 Amps. suitable for inductive loads for following poles in the existing M.C.B., D.B. with connection, testing and commissioning etc as required
a) | 2.10.1 | Single Pole | 170 | Nos | 169 | 28730
b) | 2.10.2 | Single pole and neutral | 72 | Nos | 441 | 31752
10 | 1322 | Supplying & fixing of 3 mm thick laminated hyleam sheet | 180000 | sq.cm | 0.1 | 18000
11 | 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.3.7 | 2 + 10 way/ 12 Way Double door | 12 | nos | 1344 | 16128
12 | 1.33 | Supplying and fixing of two pin 5 amps ceiling rose on the existing junction box/PVC box including connection etc as required. | 110 | Nos | 42 | 4620
13 | B.S.R.-09.sl. No. 1.34 | Supplying and fixing batten/angle holder including connection etc. as required() | 95 | Nos | 28 | 2660
14 | 1.22 | Supply fitting and fixing of metal of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required.
a) | 1.22.1 | 75 mm X 75 mm X 60 mm deep | 11 | Nos | 82 | 902
b) | 1.22.2 | 100 mm X 100 mm X 60 mm deep | 18 | Nos | 100 | 1800
c) | 1.22.3 | 150 mm X 75 mm X 60 mm deep | 21 | Nos | 103 | 2163
d) | 1.22.5 | 180 mm X 100 mm X 60 mm deep | 18 | Nos | 120 | 2160
e) | 1.22.12 | 200 mm X 250 mm X 100 mm deep | 20 | Nos | 276 | 5520
15 | 1.16 | Rewiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel / PVC conduit including dismantling as required. | 4 | Nos | 422 | 1688
16 | 1.9 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 9 | nos. | 679 | 6111
17 | B.S.R-09,sl.no. 2.5 | Providing and fixing following capacity Bus bar chamber with 4 strips of suitable size made of copper heavy duty complete with all accessories including connection earthing the body etc. as reqired.
a) | 2.5.4 | 300 amps | 2 | nos | 7646 | 15292
18 | 5.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | set | 3926 | 7852
19 | 5.7 | Supplying and laying25 mm x 5mm GI Strip at 0.50 mt below ground as strip earth electrod including soldering,etc as required | 40 | mts | 109 | 4360
20 | 5.9 | Providing and fixing 6 SWG. G.I. wire on surface or in recess for loop earthing as required | 100 | mts | 27 | 2700
21 | 5.11 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | 45 | mts | 421 | 18945
22 | As per approved rate of IGIMS | Supplying and fixing of thermal magnetic release DN-2 type Ics = 100 % Icu , conforms to IS / IEC 60947-2 & ICS 60947-2, 160 -200 amps. 36 KA MCCB as required. | 4 | No | 22500 | 90000
23 | As per approved rate of IGIMS | SS enclosure suitable for 4 pole DN type MCCBs | 4 | No | 1600 | 6400
24 |  | Opening the existing XLPE Under ground cable 1100 vols end joints from feeder pillar boxes, making the place for new XLPE under ground 1100 volts cable and making out cable end jointing with aluminum lugs of thefollowing sizes/ capacity as required (CPWD-2007, page no. 11)
| i | 2 x 10 mm.sq | 86 | set | 148 | 12728
| ii | 3.5 core 35 mm.sq | 10 | set | 270 | 2700
| iii | 3.5 core 50 mm.sq. | 8 | set | 342 | 2736
| Total Amount Rs. |  |  |  |  | 820730

## Sheet2
Bill of Electrical wiring 0f Repair & renovation of electrical Wiring/ replacement of damaged Accessories in "MDH" quarters residential complex of IGIMS, Patna
Sl.No. | DSR-14 | Items | Qty. |  | Rate | Total
1 | 1.8 | Wiring for light point/fan point /exhaust fan point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/recess P.V.C. conduit with piano type switch, phenolic laminated sheet, suitable size pvc / gi box etc. as required.
a) | 1.8.1 | Group-B | 70 | Nos. | 543 | 38010
2 | 1.12 | Wiring for light/power plug with 2 x 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/ recessed P.V.C. conduit along with 1-No. 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable for loop earthing as required. | 170 | MT | 162 | 27540
3 | 1.14 | Wiring for cirucit/sub-main wiring alongwith earth wire with the following sizes of P.V.C. insulated copper conductor, single core cable in surface/recessed pvc conduit, as required.
a) | 1.14.1 | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | 170 | MT | 106 | 18020
b) | 1.14.3 | 2 x 4 sq.mm + 1 x 4 sq.mm. earth wire | 0 | MT | 162 | 0
c) | 1.14.5 | 2 x 10 sq.mm + 1 x 10 sq.mm. earth wire | 0 | MT | 327 | 0
4 | 1.15 | Rewiring for light point /fan point /exhaust point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conducotr single core cable in existing surface/recessed P.V.C. conduit including dismantling as required.
a) | 1.15.2 | Group-B | 168 | Nos. | 303 | 50904
5 | 1.17 | Supplying and drawing following of F.R. P.V.C. inulated copper conductor single core cable in existing surface/recessed P.V.C. conduit, as required.
a) | 1.17.1 | 1 x 1.5 sq.mm | 0 | MT | 22 | 0
b) | 1.17.2 | 2 x 1.5 sq.mm | 154 | MT | 36 | 5544
c) | 1.17.3 | 3 x 1.5 sq. mm | 1054 | MT | 50 | 52700
d) | 1.17.21 | 3 x 4 sq.mm | 390 | MT | 109 | 42510
6 | 1.23 | Supplying and fixing following piano type switch/socket on the existing switch box/cover including connection etc. as required
a) | 1.13.1 | 5/6 amps.one way Switch | 220 | Nos | 33 | 7260
b) | 1.13.3 | 15/16 amps.one way Switch | 0 | Nos | 72 | 0
c) | 1.13.4 | 5/6 amps.5 pin Socket out let | 30 | Nos | 41 | 1230
d) | 1.13.5 | 15/16 amps.6 pin Socket out let | 0 | Nos | 83 | 0
7 | 1.29 | Supplying and fixing suitable sizes GI / PVC box on surface or in recess with phenolic laminated sheet cover in-front incluidng providing and fixing 5 pin 05/06 amps. Socket outlet and 05/06 amps. Piano type switch connection painting etc. as required. | 55 | Nos | 194 | 10670
8 | 1.3 | Supplying and fixing suitable size of GI / PVC box on surface or in recess with phenolic laminated sheet cover infront including providing and fixing 6 pin 5/6 amps. & 15/16 amps. Socket outlet and 15/16 amps piano type switch connection, painting etc. as required. | 51 | Nos | 276 | 14076
9 | 2.1 | Supplying and fixing following rating 240 volts 'C' series M.C.B. 5 Amps to 32 Amps. suitable for inductive loads for following poles in the existing M.C.B., D.B. with connection, testing and commissioning etc as required
a) | 2.10.1 | Single Pole | 68 | Nos | 169 | 11492
b) | 2.10.2 | Single pole and neutral | 14 | Nos | 441 | 6174
10 | 1322 | Supplying & fixing of 3 mm thick laminated hyleam sheet | 60000 | sq.cm | 0.1 | 6000
11 | 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.3.7 | 2 + 10 way/ 12 Way Double door | 13 | nos | 1344 | 17472
12 | 1.33 | Supplying and fixing of two pin 5 amps ceiling rose on the existing junction box/PVC box including connection etc as required. | 85 | Nos | 42 | 3570
13 | B.S.R.-09.sl. No. 1.34 | Supplying and fixing batten/angle holder including connection etc. as required() | 105 | Nos | 28 | 2940
14 | 1.22 | Supply fitting and fixing of metal of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required.
a) | 1.22.1 | 75 mm X 75 mm X 60 mm deep | 5 | Nos | 82 | 410
b) | 1.22.2 | 100 mm X 100 mm X 60 mm deep | 8 | Nos | 100 | 800
c) | 1.22.3 | 150 mm X 75 mm X 60 mm deep | 8 | Nos | 103 | 824
d) | 1.22.5 | 180 mm X 100 mm X 60 mm deep | 10 | Nos | 120 | 1200
e) | 1.22.12 | 200 mm X 250 mm X 100 mm deep | 11 | Nos | 276 | 3036
15 | 1.16 | Rewiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel / PVC conduit including dismantling as required. | 0 | Nos | 422 | 0
16 | 1.9 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 0 | nos. | 679 | 0
17 | B.S.R-09,sl.no. 2.5 | Providing and fixing following capacity Bus bar chamber with 4 strips of suitable size made of copper heavy duty complete with all accessories including connection earthing the body etc. as reqired.
a) | 2.5.4 | 300 amps | 0 | nos | 7646 | 0
18 | 5.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 0 | set | 3926 | 0
19 | 5.7 | Supplying and laying25 mm x 5mm GI Strip at 0.50 mt below ground as strip earth electrod including soldering,etc as required | 0 | mts | 109 | 0
20 | 5.9 | Providing and fixing 6 SWG. G.I. wire on surface or in recess for loop earthing as required | 0 | mts | 27 | 0
21 | 5.11 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | 0 | mts | 421 | 0
22 | As per approved rate of IGIMS | Supplying and fixing of thermal magnetic release DN-2 type Ics = 100 % Icu , conforms to IS / IEC 60947-2 & ICS 60947-2, 160 -200 amps. 36 KA MCCB as required. | 0 | No | 22500 | 0
23 | As per approved rate of IGIMS | SS enclosure suitable for 4 pole DN type MCCBs | 0 | No | 1600 | 0
24 |  | Opening the existing XLPE Under ground cable 1100 vols end joints from feeder pillar boxes, making the place for new XLPE under ground 1100 volts cable and making out cable end jointing with aluminum lugs of thefollowing sizes/ capacity as required (CPWD-2007, page no. 11)
| i | 2 x 10 mm.sq | 0 | set | 148 | 0
| ii | 3.5 core 35 mm.sq | 0 | set | 270 | 0
| iii | 3.5 core 50 mm.sq. | 0 | set | 342 | 0
| Total Amount Rs. |  |  |  |  | 322382

## KITCHEN BLOCK
Estimate for electrical wiring and lighting provision in the corridor between kitchen block and ward block near ramp at IGIMS, Patna-14
Sl.No. | DSR-14 | Items | Qty. |  | Rate | Total
1 | 1.8 | Wiring for light point/fan point /exhaust fan point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/recess P.V.C. conduit with piano type switch, phenolic laminated sheet, suitable size pvc / gi box etc. as required.
a) | 1.8.1 | Group-c | 16 | Each | 675 | 10800
2 | 1.4 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
a) | 1.4.2 | 2X1.5 sq.mm.+1x1.5 sq.mm.earth wire | 205 | metre | 131 | 26855
3 | 1.23. | Supplying and fixing following piano type switch/socket on the existing switch box/cover including connection etc. as required
a) | 1.23.3 | 15/16 amps.one way Switch | 2 | Each | 72 | 144
4 | 2.1 | Supplying and fixing following rating 240 volts 'C' series M.C.B. 5 Amps to 32 Amps. suitable for inductive loads for following poles in the existing M.C.B., D.B. with connection, testing and commissioning etc as required
a) | 2.10.1 | Single Pole | 1 | Each | 169 | 169
5 | 1.22 | Supply fitting and fixing of metal of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required.
a) | 1.22.1 | 75 mm X 75 mm X 60 mm deep | 2 | Each | 82 | 164
6 | 1.33 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 16 | Each | 43 | 688
7 | 1.41 | Installation, testing and commissioning of pre wired, flourescent fittings/compact flourescent fitting of all type, complete with all accessories and tube etc. directly on ceiling/wall, including connection with 1.5 sq.mm. FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 16 | Each | 91 | 1456
| Total Schedule Rs. |  |  |  | 40276
Non Schedule item
1 | 106/M/EC/EW/1019/15 | Supply of LED Tube Light 18Watt/20watt/22watt, with fixture, 1200 mm length along with intigrated driver,perfect retrofit for traditional F tube T10,Bi pin cap G13, , voltage-90-300,AC, 50 HZ, power factor greater than 0.95, colour temperature 4000 K-6500K , CRI more than 80, lumens more than 1882, Operating temperature- 20 degree Census to 60 Degree Census ) | 16 | Each | 1470 | 23520
| Total Non Schedule Rs |  |  |  | 23520
| Total Schedule+Non Schedule |  |  |  | 65266
| 1% Labour cess |  |  |  | 652.66
| Total a Amount |  |  |  | 65918.66

## B Type
Electrical wiring 0f Repair & renovation of electrical Wiring/ replacement of damaged Accessories in "B" type quarters residential complex of IGIMS, Patna
Sl.No. | DSR-14 | Items | Qty. | Unit | Rate | Total
1 | 1.8 | Wiring for light point/fan point /exhaust fan point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/recess P.V.C. conduit with piano type switch, phenolic laminated sheet, suitable size pvc / gi box etc. as required.
a) | 1.8.1 | Group-c | 120 | each | 675 | 81000
4 | 1.15 | Rewiring for light point /fan point /exhaust point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conducotr single core cable in existing surface/recessed P.V.C. conduit including dismantling as required.
a) | 1.15.2 | Group-B | 45 | Nos. | 303 | 13635
2 | 1.12 | Wiring for light/power plug with 2 x 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/ recessed P.V.C. conduit along with 1-No. 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable for loop earthing as required. | 380 | meter | 162 | 61560
3 | 1.14 | Wiring for cirucit/sub-main wiring alongwith earth wire with the following sizes of P.V.C. insulated copper conductor, single core cable in surface/recessed pvc conduit, as required.
a) | 1.14.1 | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | 390 | meter | 106 | 41340
b) | 1.14.1 | 2 x 2.5 sq mm + 1 x 2.5 sq mm | 230 | meter | 131 | 30130
c) | 1.14.5 | 2 x 10 sq.mm + 1 x 10 sq.mm. earth wire | 310 | meter | 327 | 101370
4 | 1.29 | Supplying and fixing suitable sizes GI / PVC box on surface or in recess with phenolic laminated sheet cover in-front incluidng providing and fixing 5 pin 05/06 amps. Socket outlet and 05/06 amps. Piano type switch connection painting etc. as required. | 24 | each | 194 | 4656
5 | 1.3 | Supplying and fixing suitable size of GI / PVC box on surface or in recess with phenolic laminated sheet cover infront including providing and fixing 6 pin 5/6 amps. & 15/16 amps. Socket outlet and 15/16 amps piano type switch connection, painting etc. as required. | 48 | each | 276 | 13248
6 | 2.1 | Supplying and fixing following rating 240 volts 'C' series M.C.B. 5 Amps to 32 Amps. suitable for inductive loads for following poles in the existing M.C.B., D.B. with connection, testing and commissioning etc as required
a) | 2.10.1 | Single Pole | 100 | each | 169 | 16900
b) | 2.10.2 | Single pole and neutral | 20 | each | 441 | 8820
7 | 1322 | Supplying & fixing of 3 mm thick laminated hyleam sheet | 180000 | sq.cm | 0.1 | 18000
8 | 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.3.7 | 2 + 10 way/ 12 Way Double door | 10 | each | 1344 | 13440
6 | 1.23 | Supplying and fixing following piano type switch/socket on the existing switch box/cover including connection etc. as required
a) | 1.13.1 | 5/6 amps.one way Switch | 110 | each | 33 | 3630
b) | 1.13.3 | 15/16 amps.one way Switch | 20 | each | 72 | 1440
c) | 1.13.4 | 5/6 amps.5 pin Socket out let | 32 | each | 41 | 1312
d) | 1.13.5 | 15/16 amps.6 pin Socket out let | 20 | each | 83 | 1660
14 | 1.22 | Supply fitting and fixing of metal of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required.
a) | 1.22.1 | 75 mm X 75 mm X 60 mm deep | 10 | each | 82 | 820
b) | 1.22.2 | 100 mm X 100 mm X 60 mm deep | 12 | each | 100 | 1200
c) | 1.22.3 | 150 mm X 75 mm X 60 mm deep | 16 | each | 103 | 1648
d) | 1.22.5 | 180 mm X 100 mm X 60 mm deep | 8 | each | 120 | 960
e) | 1.22.12 | 200 mm X 250 mm X 100 mm deep | 15 | each | 276 | 4140
5 | 1.17 | Supplying and drawing following of F.R. P.V.C. inulated copper conductor single core cable in existing surface/recessed P.V.C. conduit, as required.
a) | 1.17.1 | 1 x 1.5 sq.mm | 110 | meter | 22 | 2420
b) | 1.17.2 | 2 x 1.5 sq.mm | 130 | meter | 36 | 4680
c) | 1.17.12 | 3 x 2.5 sq. mm | 115 | meter | 75 | 8625
d) | 1.17.21 | 3 x 4 sq.mm | 115 | meter | 109 | 12535
9 | 1.33 | Supplying and fixing of two pin 5 amps ceiling rose on the existing junction box/PVC box including connection etc as required. | 90 | each | 42 | 3780
10 | B.S.R.-09.sl. No. 1.34 | Supplying and fixing batten/angle holder including connection etc. as required() | 90 | each | 28 | 2520
11 | Approved rate of IGIMS | 1200 mm ceiling fan, Copper armature winding with double ball bearing voltage 220v ,74 watt speed 400 RPM Air delivery 238 CFM (Havells SS390 or equivalent) | 30 | each | 2280 | 68400
12 | 1.44 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 30 | each | 95 | 2850
| Total Schedule item |  |  |  |  | 526719
| 1% Labour cess |  |  |  |  | 5267.19
| Total Amount Rs. |  |  |  |  | 531986.19
Note on B11: Qamar:

## Physiotharapy
TECHNICAL SANCTION
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Estimate for Electrical Work in Expension of Deptt. Of Physiotharapy services in Polyclinic Building 2nd & 3rd, Floor space in between Two lift pit at, I.G.I.M.S. Patna.
Sl.No. | DSR-16/BSR-09 | Item | Unit | Qty. | Rate | Total
1 | 1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a) | 1.10.3 | Group -C | point | 24 | 757 | 18168
2 | 1.14 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
a) | 1.14.2 | 2 x 2.5 sq.mm. + 1 x 2.5 sq.mm. earth wire | Meter | 35 | 137 | 4795
b) | 1.14.3 | 2 x 4 sq.mm. + 1x4 sq.mm. earth wire | Meter | 190 | 168 | 31920
c) | BSR-09, 1.7.12 | 4 x 10 sq.mm + 1 x 10 sq.mm. earth wire | Meter | 70 | 592 | 41440
3 | 1.31 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 12 | 313 | 3756
4 | 1.32 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 12 | 406 | 4872
5 | 1.25 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 8 | 288 | 2304
6 | 2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.4.6 | 6 way (4 + 18), Double door | Each | 2 | 2659 | 5318
7 | 2.1 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 2.10.1 | Single Pole | Each | 36 | 173 | 6228
b) | 2.102 | 50/63 Amps TPN | Each | 2 | 891 | 1782
8 | 2.18 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 4 | 980 | 3920
9 | 1.41 | Installation, testing and commissioning of pre wired, flourescent fittings/compact flourescent fitting of all type, complete with all accessories and tube etc. directly on ceiling/wall, including connection with 1.5 sq.mm. FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 12 | 100 | 1200
10 | 1.44 | Installation, testing and commissioning of celling fan, including wiring the down rods of standard length (upto30cm) with 1.5sqmm. FRLS PVC insulated, copper conducotor, single core cable etc. as required. | Each | 8 | 105 | 840
11 | 1.33 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 24 | 46 | 1104
12 | BSR-09, 1.34 | Supplying and fixing batten/angle holder including connection etc. as required. | Each | 8 | 28 | 224
| Total Rs. |  |  |  |  | 127871
| (B) | Non schedule Items
13 | NS Item no-02 Agr. No-53/M/EC/EW/1010/15 | 1200 mm ceiling fan, Copper armature winding with double ball bearing voltage 220v ,74 watt speed 400 RPM Air delivery 238 CFM (Havells SS390 or equivalent) | Each | 8 | 2280 | 18240
14 | NS Item no-01 Agr. No-53/M/EC/EW/1010/15 | Supply of LED Tube Light 18Watt/20watt/22watt, with fixture, 1200 mm length along with intigrated driver,perfect retrofit for traditional F tube T10,Bi pin cap G13, , voltage-90-300,AC, 50 HZ, power factor greater than 0.95, colour temperature 4000 K-6500K , CRI more than 80, lumens more than 1882, Operating temperature- 20 degree Census to 60 Degree Census ) | Each | 12 | 1470 | 17640
|  | Total Rs. |  |  |  | 35880
| (A) | shedule |  |  | 127871
| (B) | Non schedule Items |  |  | 35880
|  | Total amount Rs. |  |  | 163751
|  | 1% Labour cess |  |  | 1637.51
|  | Total amount Rs. |  |  | 165388.51

## Sheet10
1ST R A BILLElectrical wiring 0f Repair & renovation of electrical Wiring/ replacement of damaged Accessories in "MDH" quarters residential complex of IGIMS, Patna
Sl.No. | DSR-14 | Items | Qty. |  | Rate | Total
1 | 1.8 | Wiring for light point/fan point /exhaust fan point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/recess P.V.C. conduit with piano type switch, phenolic laminated sheet, suitable size pvc / gi box etc. as required.
a) | 1.8.1 | Group-B | 45 | Nos. | 543 | 24435
2 | 1.12 | Wiring for light/power plug with 2 x 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable in surface/ recessed P.V.C. conduit along with 1-No. 4 sq.mm F.R. P.V.C. insulated copper conductor single core cable for loop earthing as required. | 280 | MT | 162 | 45360
3 | 1.14 | Wiring for cirucit/sub-main wiring alongwith earth wire with the following sizes of P.V.C. insulated copper conductor, single core cable in surface/recessed pvc conduit, as required.
a) | 1.14.1 | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | 900 | MT | 106 | 95400
b) | 1.14.3 | 2 x 4 sq.mm + 1 x 4 sq.mm. earth wire | 50 | MT | 162 | 8100
c) | 1.14.5 | 2 x 10 sq.mm + 1 x 10 sq.mm. earth wire | 0 | MT | 327 | 0
4 | 1.15 | Rewiring for light point /fan point /exhaust point/call bell point with 1.5 sq.mm F.R. P.V.C. insulated copper conducotr single core cable in existing surface/recessed P.V.C. conduit including dismantling as required.
a) | 1.15.2 | Group-B | 168 | Nos. | 303 | 50904
5 | 1.17 | Supplying and drawing following of F.R. P.V.C. inulated copper conductor single core cable in existing surface/recessed P.V.C. conduit, as required.
a) | 1.17.1 | 1 x 1.5 sq.mm | 0 | MT | 22 | 0
b) | 1.17.2 | 2 x 1.5 sq.mm | 0 | MT | 36 | 0
c) | 1.17.3 | 3 x 1.5 sq. mm | 560 | MT | 50 | 28000
d) | 1.17.21 | 3 x 4 sq.mm | 390 | MT | 109 | 42510
6 | 1.23 | Supplying and fixing following piano type switch/socket on the existing switch box/cover including connection etc. as required
a) | 1.13.1 | 5/6 amps.one way Switch | 77 | Nos | 33 | 2541
b) | 1.13.3 | 15/16 amps.one way Switch | 2 | Nos | 72 | 144
c) | 1.13.4 | 5/6 amps.5 pin Socket out let | 65 | Nos | 41 | 2665
d) | 1.13.5 | 15/16 amps.6 pin Socket out let | 2 | Nos | 83 | 166
7 | 1.29 | Supplying and fixing suitable sizes GI / PVC box on surface or in recess with phenolic laminated sheet cover in-front incluidng providing and fixing 5 pin 05/06 amps. Socket outlet and 05/06 amps. Piano type switch connection painting etc. as required. | 55 | Nos | 194 | 10670
8 | 1.3 | Supplying and fixing suitable size of GI / PVC box on surface or in recess with phenolic laminated sheet cover infront including providing and fixing 6 pin 5/6 amps. & 15/16 amps. Socket outlet and 15/16 amps piano type switch connection, painting etc. as required. | 58 | Nos | 276 | 16008
9 | 2.1 | Supplying and fixing following rating 240 volts 'C' series M.C.B. 5 Amps to 32 Amps. suitable for inductive loads for following poles in the existing M.C.B., D.B. with connection, testing and commissioning etc as required
a) | 2.10.1 | Single Pole | 120 | Nos | 169 | 20280
b) | 2.10.2 | Single pole and neutral | 20 | Nos | 441 | 8820
10 | 1322 | Supplying & fixing of 3 mm thick laminated hyleam sheet | 55000 | sq.cm | 0.1 | 5500
11 | 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.3.7 | 2 + 10 way/ 12 Way Double door | 12 | nos | 1344 | 16128
12 | 1.33 | Supplying and fixing of two pin 5 amps ceiling rose on the existing junction box/PVC box including connection etc as required. | 80 | Nos | 42 | 3360
13 | B.S.R.-09.sl. No. 1.34 | Supplying and fixing batten/angle holder including connection etc. as required() | 95 | Nos | 28 | 2660
14 | 1.22 | Supply fitting and fixing of metal of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required.
a) | 1.22.1 | 75 mm X 75 mm X 60 mm deep | 3 | Nos | 82 | 246
b) | 1.22.2 | 100 mm X 100 mm X 60 mm deep | 3 | Nos | 100 | 300
c) | 1.22.3 | 150 mm X 75 mm X 60 mm deep | 2 | Nos | 103 | 206
d) | 1.22.5 | 180 mm X 100 mm X 60 mm deep | 2 | Nos | 120 | 240
e) | 1.22.12 | 200 mm X 250 mm X 100 mm deep | 1 | Nos | 276 | 276
15 | 1.16 | Rewiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel / PVC conduit including dismantling as required. | 0 | Nos | 422 | 0
16 | 1.9 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 0 | nos. | 679 | 0
17 | B.S.R-09,sl.no. 2.5 | Providing and fixing following capacity Bus bar chamber with 4 strips of suitable size made of copper heavy duty complete with all accessories including connection earthing the body etc. as reqired.
a) | 2.5.4 | 300 amps | 0 | nos | 7646 | 0
18 | 5.1 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 0 | set | 3926 | 0
19 | 5.7 | Supplying and laying25 mm x 5mm GI Strip at 0.50 mt below ground as strip earth electrod including soldering,etc as required | 0 | mts | 109 | 0
20 | 5.9 | Providing and fixing 6 SWG. G.I. wire on surface or in recess for loop earthing as required | 0 | mts | 27 | 0
21 | 5.11 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and re-filling etc. as required. | 45 | mts | 0 | 0
22 | As per approved rate of IGIMS | Supplying and fixing of thermal magnetic release DN-2 type Ics = 100 % Icu , conforms to IS / IEC 60947-2 & ICS 60947-2, 160 -200 amps. 36 KA MCCB as required. | 4 | No | 0 | 0
23 | As per approved rate of IGIMS | SS enclosure suitable for 4 pole DN type MCCBs | 4 | No | 0 | 0
24 |  | Opening the existing XLPE Under ground cable 1100 vols end joints from feeder pillar boxes, making the place for new XLPE under ground 1100 volts cable and making out cable end jointing with aluminum lugs of thefollowing sizes/ capacity as required (CPWD-2007, page no. 11)
| i | 2 x 10 mm.sq | 0 | set | 148 | 0
| ii | 3.5 core 35 mm.sq | 0 | set | 270 | 0
| iii | 3.5 core 50 mm.sq. | 0 | set | 342 | 0
| Total Amount Rs. |  |  |  |  | 384919

## Sheet11
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Estimate for Electrical repairing and renovation Work in female ward and corridore, 1st floor Ward block at, I.G.I.M.S. Patna.
Sl.No. | DSR-16 | Items | Item | Qty. | Unit | Rate | Total
1 | 1.1 |  | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a) | 1.10.3 |  | Group -C | 120 | Point | 757 | 90840
2 | 1.14 |  | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
a) | 1.14.1 |  | 2 x 1.5 sq.mm. + 1 x 1.5 sq.mm. earth wire | 280 | Meter | 112 | 31360
b) | 1.14.2 |  | 2 x 2.5 sq.mm. + 1 x 2.5 sq.mm. earth wire | 560 | Meter | 137 | 76720
c) | 1.14.3 |  | 2 x 4 sq.mm. + 1 x 4 sq.mm. earth wire | 977.378 | Meter | 168 | 164199.504
d) | 1.14.11 |  | 4 x 16 sq.mm + 2 x 6 sq.mm earth wire | 90 | Meter | 733 | 65970
3 | 1.31 |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 60 | Each | 313 | 18780
4 | 1.32 |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 60 | Each | 406 | 24360
5 | 2.4 |  | Supplying and fixing following way horizontal type three pole and neutral, sheet steel MCB distribution board 415 volts on surface / recess complete with tinned copper bus bar neutral bus bar , earth bar , din bar interconnections , powder painted including earthing etc as required. ( but without MCB/RCCB/Isolator)
a) | 2.4.6 |  | 8 way (4 + 24), Double door | 3 | Each | 3171 | 9513
6 | 2.1 |  | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 2.10.1 |  | Single Pole | 190 | Each | 173 | 32870
b) | 2.10.5 |  | Triple pole and neutral | 3 | Each | 891 | 2673
7 | 1.33 |  | s | 70 | Each | 46 | 3220
8 | 1.41 |  | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 50 | Each | 100 | 5000
10 | BSR-09, 1.34 |  | Supplying and fixing batten/angle holder including connection etc. as required. | 45 | Each | 28 | 1260
| Total Rs. | [5 empty] | 526765.504
| (B) |  | Non schedule Items
Sr. No. |  | Items | Item | Qty. | Unit | Rate | Total
11 | 58/M/EC/EW/1111/16 |  | Supply of LED Tube Light 18Watt/20watt/22watt, with fixture, 1200 mm length along with intigrated driver,perfect retrofit for traditional F tube T10,Bi pin cap G13, , voltage-90-300,AC, 50 HZ, power factor greater than 0.95, colour temperature 4000 K-6500K , CRI more than 80, lumens more than 1882, Operating temperature- 20 degree Census to 60 Degree Census ) | 77 | Each | 1470 | 113190
|  |  | Total Rs. |  |  |  | 113190
| (A) |  | Schedule Items |  |  | 526765.504
| (B) |  | Non schedule Items |  |  | 113190
|  |  | Total amount Rs. |  |  | 639955.504
| Lbour cess 1% |  |  |  |  | 6399.555
|  |  | Grand Total Amount | ₹ |  | 646355.059

## Sheet12
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Estimate of smoke evacuation system in sansetive areas of hospital and Supply fixing construction of Aluminium composite compound structure for VRV indoor at Trauma center at I.G.I.M.S. Patna.
Sl.No. | BSR-09,/DSR-14 | Item | Unit | Qty. | Rate | Total
1 | Rate Analisys | Axial unidirectional sound insulated fan in accordance with EN 12101-3. with aerofoil impeller Adjustable pitch angle, Die cast aluminium hub and blades. • Long casing, hot dip galvanized steel, to DIN EN ISO 1461. • Spun flanges for high rigidity, to Eurovent 1/2. • Terminal box in IP65 mounted at the outside of the casing for easy wiring. • Motors IP55, insulation class F, in accordance with EN 60034-5/IEC 85. • Suitable for operating temperatures of up to 55°C continuous or once for 300°C/120 min. • Inspection hole to verify correct direction of rotation. Performance tested in accordance with DIN ISO 5801, DIN 24163 and AMCA 210-99. 415 Volt, 3 phase , 2 pole impeller diameter -500 mm, 1.10 Kw , Maximum air flow 1.91cubic meter /sec, 1445 rpm, Maximum temp of transported air200 degree centigrade, Insulation class of motor-F, Enclosure class of of motor-IP 55. ( Make –System Air or equivalent reputed internationally accepted brand in smoke extraction axial fans) | Each | 9 | 336797.56 | 3031178.04
2 | Price List | Supplying & fixing Direct On Line Starter in sheet steet enclosure motor rating AC 3 duty 415 volt 50 hz 3 phase 10 HP relay range 15 amps-25 amps (L&T MK 1 DOL Cat no.MU1 DOL SS95647) or equvalant | Each | 3 | 3390 | 10170
2 | 6.14 | Supply and fixing following size and core PVC / XLPE insulated PVC sheathead ,heavy duty ,armoured electrical cable with aluminium conductor for working voltage upto and including 1100 volts (confirms to IS:1554 PART-1)
a) | 6.14.4 | 16 sq mm 4 core | Meter | 950 | 235 | 223250
3 | 2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.4.3 | 8 way (4 + 24), Double door | Each | 4 | 3171 | 12684
4 | 2.10. | supply and fixing following rating 240 volts, "C: series, miniature circuit breaker suitable for inductive loads of following poles in the exiting MCB DB complete with connections,testing and commissioning etc. As required.
a) | 2.10.1 | 50/63 amps, TPN | Each | 4 | 891 | 3564
5 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a) | 9.1.33 | 4 X16 sq. mm (28mm) | Each | 32 | 255 | 8160
6 | Rate Analisys | Supplying fixing and construction of 4 mm thick Aluminium composite compound structure for VRV indoor | Square meter | 187 | 1721 | 321827
7 | Rate Analisys | Supply and fixing of Aluminium channel of (as per IS 1868) minimum anodic coating of grade ac-15for structural support of ACP | Kg | 305 | 224 | 68320
Total Rs. | [5 empty] | 3679153.04
Labour Cess @1% | [5 empty] | 36791.5304
Total Rs. | [5 empty] | 3715944.5704
Say | [5 empty] | 3715945

## Sheet13
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Estimate for Electrical repairing Work in resarch lab biochemistry department at, I.G.I.M.S. Patna.
Sl.No. | DSR-16 | Items | Item | Unit | Qty. | Rate | Total
1 | 1.1 |  | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a) | 1.10.3 |  | Group -C | Point | 20 | 757 | 15140
2 | 1.14 |  | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0
b) | 1.14.2 |  | 2 x 2.5 sq.mm. + 1 x 2.5 sq.mm. earth wire | Meter | 45 | 137 | 6165
c) | 1.14.3 |  | 2 x 4 sq.mm. + 1 x 4 sq.mm. earth wire | Meter | 135 | 168 | 22680
d) | 1.14.10 |  | 4 x 10 sq.mm + 2 x 6 sq.mm earth wire | Meter | 35 | 536 | 18760
3 | 1.31 |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 8 | 313 | 2504
4 | 1.32 |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 8 | 406 | 3248
5 | 2.4 |  | Supplying and fixing following way horizontal type three pole and neutral, sheet steel MCB distribution board 415 volts on surface / recess complete with tinned copper bus bar neutral bus bar , earth bar , din bar interconnections , powder painted including earthing etc as required. ( but without MCB/RCCB/Isolator) |  |  |  | 0
a) | 2.4.6 |  | 8 way (4 + 24), Double door | Each | 1 | 3171 | 3171
6 | 2.1 |  | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0
a) | 2.10.1 |  | Single Pole | Each | 24 | 173 | 4152
b) | 2.10.5 |  | Triple pole and neutral | Each | 1 | 891 | 891
7 | BSR-09, 1.34 |  | Supplying and fixing batten/angle holder including connection etc. as required. | Each | 4 | 28 | 112
|  |  | Total Rs. |  |  | 76823
| Lbour cess 1% |  |  |  |  | 768.23
|  |  | Grand Total Amount |  |  | 77591.23
|  |  | Say |  |  | 68416

## Sheet14
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Estimate of smoke evacuation system in sansetive areas of hospital and Supply fixing construction of Aluminium composite compound structure for VRV indoor at Trauma center at I.G.I.M.S. Patna.
Sl.No. | BSR-09,/DSR-14 | Item | Unit | Qty. | Rate | Total
1 | Rate Analisys | Axial unidirectional sound insulated fan in accordance with EN 12101-3. with aerofoil impeller Adjustable pitch angle, Die cast aluminium hub and blades. • Long casing, hot dip galvanized steel, to DIN EN ISO 1461. • Spun flanges for high rigidity, to Eurovent 1/2. • Terminal box in IP65 mounted at the outside of the casing for easy wiring. • Motors IP55, insulation class F, in accordance with EN 60034-5/IEC 85. • Suitable for operating temperatures of up to 55°C continuous or once for 300°C/120 min. • Inspection hole to verify correct direction of rotation. Performance tested in accordance with DIN ISO 5801, DIN 24163 and AMCA 210-99. 415 Volt, 3 phase , 2 pole impeller diameter -500 mm, 1.10 Kw , Maximum air flow 1.91cubic meter /sec, 1445 rpm, Maximum temp of transported air200 degree centigrade, Insulation class of motor-F, Enclosure class of of motor-IP 55. ( Make –System Air or equivalent reputed internationally accepted brand in smoke extraction axial fans) | Each | 9 | 336797.56 | 3031178.04
2 | Price List | Supplying & fixing Direct On Line Starter in sheet steet enclosure motor rating AC 3 duty 415 volt 50 hz 3 phase 10 HP relay range 15 amps-25 amps (L&T MK 1 DOL Cat no.MU1 DOL SS95647) or equvalant | Each | 3 | 3390 | 10170
2 | 6.14 | Supply and fixing following size and core PVC / XLPE insulated PVC sheathead ,heavy duty ,armoured electrical cable with aluminium conductor for working voltage upto and including 1100 volts (confirms to IS:1554 PART-1)
a) | 6.14.4 | 16 sq mm 4 core | Meter | 950 | 235 | 223250
3 | 2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.4.3 | 8 way (4 + 24), Double door | Each | 4 | 3171 | 12684
4 | 2.10. | supply and fixing following rating 240 volts, "C: series, miniature circuit breaker suitable for inductive loads of following poles in the exiting MCB DB complete with connections,testing and commissioning etc. As required.
a) | 2.10.1 | 50/63 amps, TPN | Each | 4 | 891 | 3564
5 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a) | 9.1.33 | 4 X16 sq. mm (28mm) | Each | 32 | 255 | 8160
6 | Rate Analisys | Supplying fixing and construction of 4 mm thick Aluminium composite compound structure for VRV indoor | Square meter | 187 | 1721 | 321827
7 | Rate Analisys | Supply and fixing of Aluminium channel of (as per IS 1868) minimum anodic coating of grade ac-15for structural support of ACP | Kg | 305 | 224 | 68320
Total Rs. | [5 empty] | 3679153.04
Labour Cess @1% | [5 empty] | 36791.5304
Total Rs. | [5 empty] | 3715944.5704
Say | [5 empty] | 3715945

## smoke evacuatiuon
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Estimate of smoke evacuation system in sansetive areas of hospital and Supply fixing construction of Aluminium composite compound structure for VRV indoor at Trauma center at I.G.I.M.S. Patna.
Sl.No. | BSR-09,/DSR-14 | Item | Unit | Qty. | Rate | Total
1 | Rate Analisys | SITC of Axial unidirectional sound insulated fan in accordance with EN 12101-3. with aerofoil impeller Adjustable pitch angle, Die cast aluminium hub and blades. • Long casing, hot dip galvanized steel, to DIN EN ISO 1461. • Spun flanges for high rigidity, to Eurovent 1/2. • Terminal box in IP65 mounted at the outside of the casing for easy wiring. • Motors IP55, insulation class F, in accordance with EN 60034-5/IEC 85. • Suitable for operating temperatures of up to 55°C continuous or once for 300°C/120 min. • Inspection hole to verify correct direction of rotation. Performance tested in accordance with DIN ISO 5801, DIN 24163 and AMCA 210-99. 415 Volt, 3 phase , 2 pole impeller diameter -500 mm, 1.10 Kw , Maximum air flow 1.91cubic meter /sec, 1445 rpm, Maximum temp of transported air200 degree centigrade, Insulation class of motor-F, Enclosure class of of motor-IP 55. ( Make –System Air or equivalent reputed internationally accepted brand in smoke extraction axial fans) at different locations at IGIMS | Each | 9 | 336797.56 | 3031178.04
2 | Price List | Supplying & fixing Direct On Line Starter in sheet steet enclosure motor rating AC 3 duty 415 volt 50 hz 3 phase 10 HP relay range 15 amps-25 amps (L&T MK 1 DOL Cat no.MU1 DOL SS95647) or equvalant | Each | 3 | 3390 | 10170
3 | BSR-09 6.14 | Supply and fixing following size and core PVC / XLPE insulated PVC sheathead ,heavy duty ,armoured electrical cable with aluminium conductor for working voltage upto and including 1100 volts (confirms to IS:1554 PART-1)
a) | 6.14.4 | 16 sq mm 4 core | Meter | 950 | 235 | 223250
3 | 2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a) | 2.4.3 | 8 way (4 + 24), Double door | Each | 3 | 3171 | 9513
4 | 2.10. | supply and fixing following rating 240 volts, "C: series, miniature circuit breaker suitable for inductive loads of following poles in the exiting MCB DB complete with connections,testing and commissioning etc. As required.
a) | 2.10.1 | 50/63 amps, TPN | Each | 3 | 891 | 2673
5 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a) | 9.1.33 | 4 X16 sq. mm (28mm) | Each | 32 | 255 | 8160
6 | Rate Analisys | Supplying fixing and construction of 4 mm thick Aluminium composite compound structure for VRV indoors | Square meter | 190 | 1621 | 307990
7 | 21.1.1.1 BCD-14 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / aneling,C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) :For fixed portion Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | Kg | 254.69 | 354.8 | 90364.012
Total Rs. | [5 empty] | 3683298.052
Labour Cess @1% | [5 empty] | 32849.44
Total Rs. | [5 empty] | 3716147.492
Say | [5 empty] | 3716147

## Price bid sr no 1 of 105
INDIRA GANDHI INSTITUTE OF MEDICAL SCIENCES: SHEIKHPURA: PATNA-14
Price Bid Sr. No. -1 of Engg/105/EW/2016-17 Name of work- Electrical repairing Work in resarch lab and museum biochemistry department at, I.G.I.M.S. Patna.
Name and address of the bidder
Date and time of opening the technical bid |  |  | 16/12/2016 at 15.30 hrs
Last date for submission |  |  | 15/12/2016 till 15.30 hrs
Estimated cost |  |  | 280673/-
Cost of BOQ |  |  | ₹ | 750/-
EMD |  |  | ₹ | 5615/-
Time of completion |  |  | 15 days
Bidders are requested to quote their minimum rate in percetage above/ below or at par of our estimated rate below
Sl.No. | Items | Item | Unit | Qty. | Rate | Total
1 |  | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a) |  | Group -C | Each | 24 | 675 | 16200
2 |  | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0
a) |  | 2 x 2.5 sq.mm. + 1 x 2.5 sq.mm. earth wire | Meter | 65 | 150 | 9750
b) |  | 2 x 4 sq.mm. + 1 x 4 sq.mm. earth wire | Meter | 390 | 193 | 75270
c) |  | 4 x 10 sq.mm + 1 x10 sq.mm earth wire | Meter | 95 | 684 | 64980
3 |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 24 | 372 | 8928
4 |  | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 24 | 446 | 10704
5 |  | Supplying and fixing following way horizontal type three pole and neutral, sheet steel MCB distribution board 415 volts on surface / recess complete with tinned copper bus bar neutral bus bar , earth bar , din bar interconnections , powder painted including earthing etc as required. ( but without MCB/RCCB/Isolator) |  |  |  | 0
a) |  | 4 way (4 + 12), Double door, horizantal type | Each | 1 | 2971 | 2971
b) |  | 8 way (4 + 24), Double door , horizantal type | Each | 1 | 4655 | 4655
6 |  | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0
a) |  | Single Pole | Each | 36 | 208 | 7488
b) |  | Triple pole and neutral | Each | 2 | 1804 | 3608
7 |  | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 2 | 849 | 1698
8 |  | Supplying and fixing2 pin,6 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 20 | 35 | 700
9 |  | Supplying and fixing batten/angle holder including connection etc. as required. | Each | 4 | 48 | 192
10 |  | Supplying and fixing single wall maunted 20/22 watt LED type batten fitting complete with electronic driver and LED tube etc directly on wall /ceiling including connection with 1.5 sq mm FR PVC insulated copper conductor and the earthing body etc as required | Each | 16 | 2542 | 40672
11 |  | Earthing with Copper earth Plate 600mm x 600mm x 3mm thick including accesssories, and providing masonary enclosure with cover plate having locking arrangement and watering pipe 2.7 meter long etc with charcoal /cock and salt as required .etc. ) | Each | 1 | 11703 | 11703
12 |  | Providing and laying 25 mm x 5 mm Copper strip in 40 mm dia G.I. pipe from earth electrode including connectionwith brass nut bolt spring washer excavation and refilliung etc as requiredpipe from earth electrode, as required. | Meter | 5 | 1131 | 5655
13 |  | Providing and fixing 4 mm dia copper wire on surface or in recess for loop reathing et as requiredsubmain wiring/ cable as required | Meter | 120 | 106 | 12720
|  | Total Rs. | 277894
|  | 1% Labour cess | 2778.94
|  | Grand Total Amount | 280672.94
|  | Say | 280673
Rates quoted by the bidder
% above the estimated cost
or
% below the estimated cost
or
at estimated rate
Signature and seal of the contractor